AIR TO WATER HEAT PUMP

Touch Screen Manual for Heat Pump Systen

V.2505

Heat Pump Models:

HSL08V-DPANW

HSL10V-DPANW

HSL12V-DPANW

HSL15V-DPANW

Before operating the system, please read these operating instructions thoroughly and keep them for future reference.

Index

1 Home Page	5

2 Function Overview	5

3 Mode Switching	5

4 Sleep Mode	6

4.1 Sleep Mode Activation (Switch)	6

4.2 Sleep Mode Time Configuration	6

4.3 Sleep Mode Compressor Maximum Operation	6

4.4 Sleep Mode Fan Maximum Operation Speed	6

5 Timer Mode	7

5.1 Timer Activation (Switch)	7

5.2 Timer Configuration	7

6 Function Menu	7

7 Heating/Cooling Circuit 1 (Heating)	8

7.1 Temperature compensation function	8

7.2 Heating Target Temperature	9

7.3 Real-Time Heating Operation Temperature	9

7.4 Current Ambient Temperature	9

7.5 Upper Limit for Water Temperature	9

7.6 Lower Limit for Water Temperature	9

7.7 Lower Limit for Ambient Temperature	9

7.8 Upper Limit for Ambient Temperature	9

8 Heating/Cooling Circuit 1 (Cooling)	9

8.1 Temperature compensation function	10

8.2 Cooling Target Temperature	10

8.3 Real-Time Cooling Operation Temperature	10

8.4 Current Ambient Temperature	10

8.5 Upper Limit for Water Temperature	10

8.6 Lower Limit for Water Temperature	10

8.7 Lower Limit for Ambient Temperature	10

8.8 Upper Limit for Ambient Temperature	10

9 Heating/Cooling Circuit 2 (Heating)	10

10 Heating/Cooling Circuit 2 (Cooling)	11

11 Domestic Hot Water Setting	12

11.1. Domestic Hot Water Temperature Differential Control	12

11.2. Hot Water Target Value 	12

11.3. Hot Water Maximum Temperature Setting	12

11.4. Hot Water Circulation Function	12

11.5. Hot Water Circulation Pump Operation Time	12

11.6. Hot Water Circulation Pump Interval Time	12

12 Holiday Mode Setting	13

12.1. Holiday Mode Activation (Switch)	13

12.2. Holiday Mode Start Time Configuration	13

12.3. Holiday Mode End Time Configuration	13

12.4. Scheduled Startup Configuration	13

12.5. Heating Target Temperature Reduction	13

12.6. Cooling Target Temperature Increase	13

12.7. Hot Water Target Temperature Reduction	13

13 Hot Water Anti-Legionella Function Setting	14

13.1. Hot Water Anti-Legionella Function Activation (Switch) 	14

13.2. Hot Water Anti-Legionella Target Temperature 	14

13.3. Scheduled Anti-Legionella Time	14

13.4. Anti-Legionella Interval Time	14

14 Auxiliary Heat Source Settings 	15

14.1. Boiler Configuration	15

14.2. Boiler Startup Outdoor Temperature Setting	15

14.3. Boiler Switchover Function	15

14.4. Auxiliary Electric Heating Configuration	15

14.5. Auxiliary Electric Heating Power	15

14.6. Hot Water Electric Heating Configuration	15

14.7. Hot Water Electric Heating Power	15

14.8. Defrost Electric Heating Configuration	15

14.9. Defrost Electric Heating Power	15

15 Energy Management 	16

16 Solar Energy Application Settings	16

16.1. Solar Application Hot Water Switch	16

16.2. Water Pump Temperature Difference Off	16

16.3. Solar Pump Heating Upper Limit	17

16.4. Solar Pump Start Setting	17

16.5. Solar Pipeline Anti-Freeze Outdoor Temperature Setting	17

16.6. Solar Pump Anti-Freeze Interval Time	17

16.7. Solar Application Heating Switch	17

16.8. Solar Heating Shutdown Temperature Difference	17

16.9. Solar Heating Upper Limit	17

16.10. Solar Heating Start Setting Value	17

17 Running State	17

18 Fault Inquiry	20

18.1 Auto Reset Alarms	21

18.2 Manual Reset Alarms	22

18.3 Alarm Code And Description	22

19 Service Level Parameters	24

20 Factory Level Parameters	25

21 Pump Settings	25

21.1. Pump Models	26

21.2. Pump Configuration	26

21.3. Pump PWM Upper Limit	26

21.4. Pump PWM Lower Limit	26

22 SG-Ready Function	26

22.1. SG-Ready Function	27

22.2 SG Heat/Cool Temperature Range	27

22.3 SG Hot Water Temperature Range	27

23 One Click Exhaust	27

23.1. Cooling/Heating Circuit Exhaust Function Switch	28

23.2. Domestic Hot Water Circuit Exhaust Function Switch	28

23.3. Automatic Exhaust Time Setting	28

24 Installation Configuration	28

25 System Configuration	29

25.1. Time Setting	29

25.2. Off Screen Setting	29

25.3. Brightness Setting	29

25.4. Language Settings	29

26 App. Control Setup	30

1 Home Page

2 Function Overview

| No. | Icon | Function |
| --- | --- | --- |
| 1 |  | Heating Mode |
| 2 |  | Cooling Mode |
| 3 |  | Heating + Hot Water |
| 4 |  | Cooling + Hot Water |
| 5 |  | Defrosting |
| 6 |  | Anti-Legionella |
| 7 |  | Holiday Mode |

| No. | Icon | Function |
| --- | --- | --- |
| 8 |  | Power Lock |
| 7 |  | Hot Water Mode |
| 10 |  | Electric Heating |
| 11 |  | Fault Inquiry |
| 12 |  | Timer Mode |
| 13 |  | Power On/Off |
| 14 |  | Operation Flow Diagram |

3 Mode Switching

The unit offers five modes: Heating Mode, Cooling Mode, Hot Water Mode, Heating + Hot Water Mode, Cooling + Hot Water Mode. Upon selecting a mode, the system will stop operation briefly to switch modes. After switching, the refrigerant flow diagram will reflect the selected heating or cooling mode.

4 Sleep Mode

4.1 Sleep Mode Activation (Switch)

Sleep mode must be enabled for the system to transition into sleep mode at the configured time.

4.2 Sleep Mode Time Configuration

You can set two time intervals for sleep mode. Tap the time fields to access the configuration interface. The left field indicates the start time, and the right field indicates the end time.

4.3 Sleep Mode Compressor Maximum Operation

This feature configures the maximum compressor frequency during sleep mode. Adjustable range: 20Hz–90Hz (default: 70Hz).

4.4 Sleep Mode Fan Maximum Operation Speed

Configures the maximum fan speed during sleep mode.

### Adjustable range: 300–350

### (default:HSL08V-D/ HSL08V-D  300;

### HSL12V-D/ HSL15V-D  350)

### 5 Timer Mode

5.1 Timer Activation (Switch)

Timer mode includes three modes: Cooling Timer, Heating Timer, Hot Water Timer. Each has a dedicated interface accessible via a left/right toggle. Timer mode, time settings, and mode switching have independent toggle switches. Only enabled timers will operate based on the set schedule.

5.2 Timer Configuration

You can configure up to four time intervals. Tap the time fields to access the configuration interface.

6 Function Menu

7 Heating/Cooling Circuit 1 (Heating)

7.1 Temperature compensation function

When temperature compensation is enabled, the target temperature cannot be set. It will calculate the actual target temperature using formula 1 and display it to Target set temperature.

(Formula 1) Actual target temperature=upper limit of water temperature - (ambient temperature - lower limit of ambient temperature) * slope

(Formula 2) Slope=(upper limit of water temperature - lower limit of water temperature)/(upper limit of ambient temperature - lower limit of ambient temperature)

7.2 Heating Target Temperature

When temperature compensation is not enabled, this parameter can be set to change the target temperature.

7.3 Real-Time Heating Operation Temperature

Displays the real-time target heating temperature adjusted by the program based on temperature compensation and other restrictions.

7.4 Current Ambient Temperature

Displays the current ambient temperature.

7.5 Upper Limit for Water Temperature

Sets the upper limit for heating target temperature when temperature compensation function is active.

7.6 Lower Limit for Water Temperature

Sets the lower limit for heating target temperature when temperature compensation function is active.

7.7 Lower Limit for Ambient Temperature

Sets the lower limit for ambient temperature adjustment during temperature compensation.

7.8 Upper Limit for Ambient Temperature

Sets the upper limit for ambient temperature adjustment during temperature compensation.

8 Heating/Cooling Circuit 1 (Cooling)

8.1 Temperature compensation function

When temperature compensation is enabled, the target temperature cannot be set. It will calculate the actual target temperature using formula 1 and display it to Target set temperature.

(Formula 1) Actual target temperature=upper limit of water temperature - (ambient temperature - lower limit of ambient temperature) * slope

(Formula 2) Slope=(upper limit of water temperature - lower limit of water temperature)/(upper limit of ambient temperature - lower limit of ambient temperature)

8.2 Cooling target temperature setting

When temperature compensation is not enabled, this parameter can be set to change the target temperature.

8.3 Real-Time Cooling Operation Temperature

Displays the real-time target cooling temperature adjusted by the program based on temperature compensation and other restrictions.

8.4 Current Ambient Temperature

Displays the current ambient temperature.

8.5 Upper Limit for Water Temperature

Sets the upper limit for cooling target temperature when temperature compensation function is active.

8.6 Lower Limit for Water Temperature

Sets the lower limit for cooling target temperature when temperature compensation function is active.

8.7 Lower Limit for Ambient Temperature

Sets the lower limit for ambient temperature adjustment during temperature compensation.

8.8 Upper Limit for Ambient Temperature

Sets the upper limit for ambient temperature adjustment during temperature compensation.

9 Heating/Cooling Circuit 2 (Heating)

After activation, it is used to configure the heating temperature control and temperature compensation of the second zone. At the same time, circuit 1 will have an additional mixing valve option. Opening the mixing valve on either side will control the temperature in the low-temperature zone, while the other side will control the target temperature in the high-temperature zone. (For example, circuit 2 opens the mixing valve, all settings in circuit 2 control the temperature in the low-temperature zone, and all settings in circuit 1 control the temperature in the high-temperature zone)

10 Heating/Cooling Circuit 2 (Cooling)

After activation, it is used to configure the cooling temperature control and temperature compensation of the second zone. At the same time, circuit 1 will have an additional mixing valve option. Opening the mixing valve on either side will control the temperature in the low-temperature zone, while the other side will control the target temperature in the high-temperature zone. (For example, circuit 2 opens the mixing valve, all settings in circuit 2 control the temperature in the low-temperature zone, and all settings in circuit 1 control the temperature in the high-temperature zone)

11 Domestic Hot Water Setting

11.1 Domestic Hot Water Temperature Differential Control

ON: When the hot water temperature (HT) ≤ ST09 - ST10.

OFF: When the hot water temperature (HT) > ST09.

(Default: ST09 = 60°C, ST10 = 5°C)

11.2 Hot Water Target Value

Specifies the target temperature for domestic hot water heating, applicable for standalone operation or combined with electric heating.

11.3 Hot Water Maximum Temperature Setting

Defines the upper limit for domestic hot water temperature.

11.4 Hot Water Circulation Function

Activating the hot water circulation pump keeps water in the pipes at an appropriate temperature, minimizing waiting time for hot water and reducing water wastage. This ensures hot water is available on demand.

The hot water circulation pump operates only when the hot water switch is ON (during hot water heating or standby modes).

11.5 Hot Water Circulation Pump Operation Time

Specifies the duration of each operation cycle for the hot water circulation pump.

11.6 Hot Water Circulation Pump Interval Time

Specifies the interval time between consecutive operations of the hot water circulation pump.

12 Holiday Mode Setting

12.1 Holiday Mode Activation (Switch)

Allows the heat pump to operate in holiday mode.

12.2 Holiday Mode Start Time Configuration

Sets the start time for holiday mode.

12.3 Holiday Mode End Time Configuration

Sets the end time for holiday mode.

12.4 Scheduled Startup Configuration

If scheduled startup is enabled, the heat pump will automatically resume operation before the end of holiday mode to ensure sufficient heating and hot water supply.

12.5 Heating Target Temperature Reduction

Adjusts the heating target temperature by a preset reduction value when temperature reduction mode is enabled.

12.6 Cooling Target Temperature Increase

Adjusts the cooling target temperature by a preset increase value when temperature reduction mode is enabled.

12.7 Hot Water Target Temperature Reduction

Adjusts the hot water target temperature by a preset reduction value when temperature reduction mode is enabled.

13 Hot Water Anti-Legionella Function Setting

13.1 Hot Water Anti-Legionella Function Activation (Switch)

Enables the Anti-Legionella Function for hot water.

13.2 Hot Water Anti-Legionella Target Temperature

Specifies the target temperature for hot water anti-legionella, including temperatures achieved through heat pump and electric heating operation.

13.3 Scheduled Anti-Legionella Time

Sets the start time for the hot water anti-legionella function.

13.4 Anti-Legionella Interval Time

Defines the interval time between anti-legionella cycles for domestic hot water.

14 Auxiliary Heat Source Settings

14.1 Boiler Configuration

### Specifies whether a boiler is integrated into the system. Boiler-related settings take effect only if this option is configured.

14.2 Boiler Startup Outdoor Temperature Setting

The boiler activates when the outdoor temperature is less than or equal to this set value.

14.3 Boiler Switchover Function

The boiler replaces the compressor under two conditions:1.The current mode is heating. 2.The outdoor temperature is less than or equal to the boiler startup setting.

14.4 Auxiliary Electric Heating Configuration

Specifies whether auxiliary electric heating is integrated.

14.5 Auxiliary Electric Heating Power

14.6 Hot Water Electric Heating Configuration

14.7 Hot Water Electric Heating Power

14.8 Defrost Electric Heating Configuration

14.9 Defrost Electric Heating Power

15 Energy Management

16 Solar Energy Application Settings

16.1 Solar Application Hot Water Switch

Activates solar water heating, independent of the current mode (heating/cooling) or the

system’s ON/OFF status. Only one solar application—hot water or heating—can operate at a time. Enabling solar hot water will automatically disable solar heating.

16.2 Water Pump Temperature Difference Off

Defines the temperature differential between the solar temperature (B3 sensor) and hot water. When the differential exceeds this set value, the solar function shuts off.

16.3 Solar Pump Heating Upper Limit

If the buffer tank temperature (B2 sensor) exceeds the solar heating upper limit for 5 minutes, the solar pump shuts off. Similarly, if the hot water temperature exceeds the solar heating upper limit, the solar pump shuts off.

(Default upper limit: 70°C; adjustable range: 40°C–90°C)

16.4 Solar Pump Start Setting

The solar pump activates when the temperature difference between the solar temperature (B3 sensor) and the buffer tank temperature (B2 sensor) exceeds the set activation threshold. The solar pump will not operate during cooling mode.

16.5 Solar Pipeline Anti-Freeze Outdoor Temperature Setting

When the outdoor temperature falls below the set anti-freeze value for 1 minute, the solar pump stops operating.

16.6 Solar Pump Anti-Freeze Interval Time

Specifies the interval time between anti-freeze operations for the solar pump. After the interval time is reached, the solar pump operates for 3 minutes before stopping. This repeats until the outdoor temperature rises above (anti-freeze value + 1°C).

16.7 Solar Application Heating Switch

Only one solar application—hot water or heating—can operate at a time. Enabling solar heating will automatically disable solar hot water.

16.8 Solar Heating Shutdown Temperature Difference

Specifies the temperature difference for shutting down the solar heating application.

16.9 Solar Heating Upper Limit

Defines the upper temperature limit for solar heating.

16.10 Solar Heating Start Setting Value

Specifies the temperature difference required to activate solar heating.

17 Running State

The running state interface consists of three pages. Navigate between pages by swiping the screen.

Press , it displays the unit measured temperature sensors value, digital switch on/off state, components on/off state.

| No. | abbreviation | description |
| --- | --- | --- |
| 1 | RT | Indoor return water temperature |
| 2 | ST. | Indoor outlet water temperature |
| 3 | OT. | Outdoor temperature |
| 4 | ET | Return air temperature |
| 5 | PT | Exhaust temperature |
| 6 | LPS | Low pressure |
| 7 | HPS | High pressure |
| 8 | water flow | Water flow feedback |
| 9 | Evaporation temp. | Evaporating temperature |
| 10 | Discharge temp. | Condensing temperature |
| 11 | Fan1 speed | Fan 1 speed feedback |
| 12 | Fan2 speed | Fan 2 speed feedback |
| 13 | EEV1 steps | EEV1 opening degree |
| 14 | EEV2 steps | EEV2 opening degree |
| 15 | Mixing valve opening | Proportional water valve opening |
| 16 | EEV1 SH | EEV1 Superheat |
| 17 | EEV2 SH | EEV2 Superheat |
| 18 | Comp. operating freq | Compressor frequency |
| 19 | Solar Temp. | Solar temperature |
| 20 | RT(Main board) | Buffer water tank temperature |
| 21 | LT zone mixing temp. | Low temperature zone mixed water temperature |
| 22 | HT zone mixing temp. | Temperature of mixed water in high temperature zone |
| 23 | 4-way valve | four-way valve |
| 24 | Pump running | Indoor water pump operation |
| 25 | DHW switch | Hot water switch |
| 26 | H/C switch | Heat pump startup |
| 27 | DefrostEH | Defrosting electric heating |
| 28 | AH | Auxiliary electric heating |
| 29 | DHWEH | Hot water and electricity heating |
| 30 | DHW circ. pump | Hot water circulating pump |
| 31 | DHW 3-way value | Hot water three-way valve |
| 32 | LT zone control signal | Low temperature zone control signal |
| 33 | HT zone control signal | High temperature zone control signal |
| 34 | Mixing pump | Partition water pump |
| 35 | Solar pump | Solar Water Pump |
| 36 | Work status | Host status |

18 Fault Inquiry

When a fault occurs in the system, the fault event logs the trigger time based on the system's internal clock and displays the fault code as the warning message. Once the fault is resolved, the release time will be recorded in the designated column.

The Fault Inquiry interface can be navigated by swiping left or right. Swiping right will move to the second page, and when on the second page, swiping left will return to the first page. The first page is CURRENT FAULT,The second page is Historical faults.

The alarms are divided into two groups: auto reset alarms and manual reset alarms.

1.Auto reset alarm, the user is not required to acknowledge and reset it.

2.The unit will automatically restart once the alarm status disappears.

3.Once a manual reset alarm is detected, the system will stop automatically. The user needs to record and contact the supplier on actions what to do.

When an alarm is detected, the  icon will continuously flash.

18.1 Auto Reset Alarms

The following are codes for auto reset alarms with their meanings.

| Codes | Meaning |
| --- | --- |
| AL01 | Low pressure |
| AL02 | High pressure |
| AL03 | Low outlet water temperature (ST<AR01 default 5.5) |
| AL05 | High outlet water temperature (ST>AR03 default 72) |
| AL17 | Water flow is short |
| WN01 | Antifreeze |
| AL20 | Low evaporation temperature (only cooling mode) |
| AL21 | High discharge gas temperature |
| AL57 | inverter offline |
| AL30 | Touch screen and main board communication trouble. |
| AL00 | Communication failure between main control board and screen |
| ALEP | Main control board memory EPROM failure |
| AL79 | Water pump fault |

Alarms relating to inverter board (auto reset)

| AL98 | Inverter board fault alarm |
| --- | --- |
| AL100 | IPM overcurrent |
| AL101 | comp. drive failure |
| AL102 | comp. overcurrent |
| AL103 | power phase loss |
| AL104 | IPM current sampling error |
| AL105 | radiator overheat |
| AL106 | pre-charging failure |
| AL107 | DC bus overvoltage |
| AL108 | DC bus under voltage |
| AL109 | AC input under voltage |
| AL110 | AC input overcurrent |
| AL111 | voltage sampling error |
| AL112 | Fan motor 1 fault |
| AL113 | temp. sensor error |
| AL114 | Fan motor 2 fault |
| AL115 | communication fault |
| AL116 | IPM module overheat |
| AL117 | Fan motor 1 fault |
| AL118 | Fan motor 2 fault |

18.2 Manual Reset Alarms

The following are codes for manual reset alarms with their meanings.

| Codes | Meaning |
| --- | --- |
| AL18 | Low pressure alarms times within 24 hours is over the limit |
| AL19 | High pressure alarms times within 24 hours is over the limit |
| AL31 | Low evaporation temperature alarm times within 24 hours is over the limit |

18.3 Alarm code and description

1.) Low pressure protection (Code: AL01)

After starting the compressor, it checks the low pressure after AR09 delay. If LPS≤AR31 (default 0.3) in continual 120 seconds, then compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL01 display on the touch screen.  After LPS≥AR31+AR32 (default 0.3) in continual 10 seconds, the unit returns to normal operation.

2.) High pressure protection (Code: AL02)

It does not trigger high pressure protection on defrosting process and within 10 seconds after end of defrosting.

At other time if HPS≥AR33 (default 30) in continual 5 seconds, the compressor is switched off, after 5 seconds' delay, the fan motor is switched off, other parts keep their original state. Alarm code AL02 display on the touch screen. After HPS≤AR33-AR34 (default 3), the unit re turns to normal operation.

3.) Low pressure protection (serious) (Code: AL18)

In 24 hours' time, if AL01 is triggered over AR06 (default 4) times, manual reset alarm AL18 is triggered,

then compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL18 display on the touch screen.

4.) High pressure protection (serious) (Code: AL19)

In 24 hours’ time, if AL02 is trigger over AR07 (default 6) times, manual reset alarm AL19 is triggered,

the compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL19 displays on the touch screen.

5.) Water flow protection (Code: AL17)

A.) AR04 (default 120s) time delay after circulation pump is switched on and circulation pump PWM output is 100% in continual 5 seconds, if feedbacked pump flow is lower than minimum flow rate EV07(cooling/defrosting) or EV25 (heating) *0.8 in continual 5 seconds, AL17 alarm is triggered.

B.) On the running process, when pump PWM output is 100%, if feedbacked pump flow is lower than EV07 (cooling/defrosting) or EV25 (heating)*0.8 in continual 5 seconds, AL17 alarm is triggered.

the compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL17 displays on the touch screen. Unit could return to normal operation if feedbacked pump flow is over EV06/EV25 in continual 5 seconds.

6.) Indoor circuit anti-freezing protection (code：WN01）

1.) If pump has been switched off over 30 minutes and OT<2, pump is switched on and runs with PWM 100%. 180 seconds later, if RT>12, pump is switched off. If RT<10, WN01 warning is triggered and unit is switched on to run on heating mode until RT＞20℃ ,then warning is reset.

2.) If RT sensor is faulted, ST is used instead of RT for anti-freezing protection water temperature reference. If ST sensor is faulted too when OT<2, pump runs continually with PWM 100%.

7.) High discharge gas temperature protection（code:AL21）

If Discharge gas temperature PT>105 in continual 5 seconds, high Discharge gas temperature protection alarm AL21 is triggered,

the compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL21 displays on the touch screen.

It will recover to normal operation if PT<85 in continual 5 seconds.

8.) Low evaporation temperature protection (Code: AL20)

The protection function will be valid on COOLING mode .AL20 low evaporation temperature protection is triggered when condition below is met:

1.) LPS ≤-2 in continual 60 seconds；

2.)LPS≤-4 in continual 40 seconds；

3.)LPS≤-6 in continual 10 seconds；

4.) outlet water temp. < 8℃

the compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL20 displays on the touch screen. It will recover to normal operation 5 minutes later.

9.) Low evaporation temperature protection (serious) (Code: AL31)

In 24 hours’ time, if AL20 is trigger over 3 times, manual reset alarm AL31 is triggered,

the compressor is switched off, 5 seconds later, fan motor is switched off, other parts keep their original state. Alarm code AL31 displays on the touch screen.

10.) Low outlet water temperature protection (Code: AL03)

If ST≤AR01 (default 5.5) and LPS < 0℃  in continual 5 seconds, the compressor is switched off, after 5 seconds' delay, the fan motor is switched off, water pump runs with PWM 100%, other parts keep their original state. Alarm code AL03 displays on the touch screen. It records the instant inlet water temperature RT1 when unit just stops and returns to normal working after inlet water temperature RT≥RT1+ ST03.

11.) High outlet water temperature protection (Code: AL05)

If ST≥ AR03 (default 72) in continual 5 seconds, the compressor is switched off, after 5 seconds delay, the fan motor is switched off, water pump runs with PWM 100%, other parts keep their original state. Alarm code AL05 display on touch screen. It records instant inlet water temperature RT2 when unit just stops and returns to normal working after inlet water temperature RT≤RT2-ST04.

12.) Display offline - Touch screen and main board communication trouble.

After this trouble happen, unit still can work normally but the touch screen can not be used to operate the unit.

13.) Temperature Sensor fault (auto reset)

If the temperature sensor is below -35C or higher than 120C , sensor fault is triggered.

| sensor | code | Unit's action to deal with the fault |
| --- | --- | --- |
| inlet water (RT) | AL71 | ST replaces RT as temperature control reference. control water temperature +5C on heating mode, -5C on cooling mode. If ST sensor faulted too, unit is switched off. |
| outlet water (ST) | AL72 | Cooling mode is invalid Heating and DHW mode is valid ,no high outlet water temperature protection and pump PWM = 100%. |
| ambient (OT) | AL73 | T(heating)=ST02 Aux. electric backup heater, crankcase heater and anti-freezing function etc works without OT condition limitation. |
| hot water (HT) | AL74 | Hot water mode is invalid. Alarm code does not display if SF05=0. |
| discharge (PT) | AL75 | Switch off the unit |
| suction pressures (LPS) | AL37 | Switch off the unit |
| discharge pressure (HPS) | AL38 | Switch off the unit |
| suction gas (ET) | AL76 | Relative function is canceled. |

19 Service Level Parameters

The service level parameter interface can be navigated by swiping left or right. Swiping right will move to the second page, and when on the second page, swiping left will return to the first page.

Installer would need to adjust some parameter value to let the unit run in the best conditions.

20 Factory Level Parameters

For safety purposes, accessing the factory level parameter settings requires a password. Only authorized personnel can modify these settings within the factory configuration interface.

21 Pump Settings

21.1 Pump Models

There are seven available pump models: APE25-8-130L, APF25-8-130E, APF25-10-130E, APF25-12-130E, HBF25-105-130, HBGF25-80-130, HBGF25-125-130, UPMF20-125-PCI.

21.2 Pump Configuration

Pump configuration options include: outside/ within

21.3 Pump PWM Upper Limit

Specifies the maximum output value of the pump.

Default: 100%

Adjustable Range: 10%–100%

21.4 Pump PWM Lower Limit

Specifies the minimum output value of the pump.

Default: 70%

Adjustable Range: 10%–100%

22 SG-Ready Function

22.1 SG-Ready Function

The SG-Ready label, issued by the German Heat Pump Association, identifies heat pumps with customized interfaces capable of grid load management. This enhances grid utilization, contributing to the efficient and economical operation of grid infrastructure.

22.2 SG Heat/Cool Temperature Range

When grid load is low and the SG function is activated:

Heating: Target temperature is adjusted by adding the SG heating range. If the adjusted value exceeds the maximum heating setting, the system operates at the maximum heating setting.

Cooling: Target temperature is adjusted by subtracting the SG cooling range. If the adjusted value exceeds the minimum cooling setting, the system operates at the minimum cooling setting.

The startup condition is controlled based on the new target temperature.

22.3 SG Hot Water Temperature Range

When grid load is low and the SG function is activated:

Hot water is controlled based on the maximum hot water setting. After the heat pump completes heating, the electric heater raises the temperature to the target value.

The startup condition is controlled based on the new target temperature.

23 One Click Exhaust

23.1 Cooling/Heating Circuit Exhaust Function Switch

When the exhaust function is activated, the system pump operates at high speed while the compressor and outdoor fan remain off. This ensures that no air remains in the water circuit, as air presence can reduce water flow. Excessive air can trigger a water flow fault (Fault Code: AL17) and degrade heating or cooling performance.

23.2 Domestic Hot Water Circuit Exhaust Function Switch

The one click exhaust for the domestic hot water circuit operates similarly to the cooling/heating circuit. Excessive air in the hot water pipes reduces the effective flow area, leading to decreased hot water flow, air blockages, and an inability to reach the target temperature.

23.3 Automatic Exhaust Time Setting

Specifies the duration for each exhaust operation.

24 Installation Configuration

25 System Configuration

25.1 Time Setting

Configure the RTC (Real-Time Clock) to ensure accurate timing. Users must set the local time after the initial installation. RTC time settings are critical for features like hot water scheduling, vacation mode, and night mode timing.

25.2 Off Screen Setting

To extend the screen's lifespan and minimize unnecessary display activity, an off screen timer can be configured.

Users can define the screen sleep duration within a range of 30–180 seconds.

Default setting: 60 seconds.

25.3 Brightness Setting

Adjust the screen's backlight brightness to match user preferences.

Brightness adjustment range: 20%–100%.

Default setting: 90%.

25.4 Language Settings

The system supports five language options: English, German

26 App. control setup

Heat pump app control:

Tuya app install

You can download the App by searching “Tuya Smart” in mobile app stores or scanning the following QR code for Android system.

1.Click “Register” and read the Privacy Policy after it pops up. Click “Agree” and enter the registration page.

2.You can use email or mobile number as your account to register.

3.Enter the verification code and turn to the password setting page. Set your password as required and click “Done”.

4.Open the "Tuya Smart" app, tap the "+" icon in the upper-right corner, select"Add Device", then choose"Smart Heat Pump (Wi-Fi)"under the "Large Appliances"category.

5.Enter your Wi-Fi network name (SSID) and password, then tap"Next".Tap "Confirm Indicator Blinking"to verify device is in pairing mode.

Note: Youmust select a 2.4GHz Wi-Fi network, otherwise the connection will fail.

6.Select "Slow Blink", then tap"Go to Connect".

7.After successful Wi-Fi connection, a pop-up notification will appear. Upon completion, a  indicator in the top-right corner will confirm the connection.​