## H-C circuit1
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | unit
ST01 | Cooling mode set point | 13 | ST11 | ST12 | ℃ | Target temperature value in cooling mode
ST02 | Heating mode set point | 40 | ST13 | ST14 | ℃ | Target temperature value in heating mode
ST03 | Adjustable temperature range in cooling mode | 2 | 1 | 10 | ℃ | No setting required
ST04 | Adjustable temperature range in heating mode | 2 | 1 | 10 | ℃
ST11 | Cooling minimum set point | 12 | 0 | 40 | ℃
ST14 | Heating maximum setting point | 65 | 20 | 80 | ℃
1. Temperature Compensation 1）To use temperature compensation, first turn on the temperature compensation switch. 2) Set the X-axis and Y-axis coordinates corresponding to the curve on the right. The heat pump target value will automatically adjust according to the set curve; (Formula 1) Actual target temperature=upper limit of water temperature - (ambient temperature - lower limit of ambient temperature) * slope (Formula 2) Slope=(upper limit of water temperature - lower limit of water temperature)/(upper limit of ambient temperature - lower limit of ambient temperature) 2. The temperature compensation setting operation for H/C circuit 1 and H/C circuit 2 is the same.

## H-C circuit2
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
ST01L | Cooling mode set point | 13 | ST11 | ST12 | ℃ | Low-temperature zone cooling target value
ST02L | Heating mode set point | 40 | ST13 | ST14 | ℃ | Low-temperature zone heating target value
ST03 | Adjustable temperature range in cooling mode | 2 | 1 | 10 | ℃ | No setting required
ST04 | Adjustable temperature range in heating mode | 2 | 1 | 10 | ℃
ST11 | Cooling minimum set point | 12 | 0 | 40 | ℃
ST14 | Heating maximum set point | 65 | 20 | 80 | ℃
SF303 | Zone temperature control function activated | 0(Off) | 0(Off) | 1(On) |  | Zone control function switch
1. Zone Temperature Control When the heat pump needs to provide different control temperatures to two heating terminals simultaneously, the zone temperature control function is required: 1) Turn on the function switch; 2) Open the mixing valve switch. At this point, H/C circuit 2 will act as the heat source for the low-temperature heating zone, and combined with the mixing valve opening setting, the heating water temperature will be lowered to the set target value for the low-temperature heating zone.

## DHW
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
User Parameters
ST09 | Domestic hot water temperature set point | 50 | 20 | 75 | ℃ | Domestic hot water target value
ST10 | Domestic hot water temperature range | 5 | 1 | 10 | ℃ | Domestic hot water restart temperature difference
ST16 | Domestic hot water maximum setting point | 70 | 20 | 80 | ℃ | No setup required
Hot water circulation switch
ST33 | Hot water circulation pump interval time | 15 | 0 | 180 | Min.
ST34 | Hot water circulation pump operating time | 3 | 0 | 180 | Min.
ST118 | Hot water temperature sensor compensation value | 0 | -10 | 10 | ℃ | Error compensation for hot water temperature sensor detection value
Hot water circulation pump operation rules When the setting values of ST33 and ST34 are not 0, if the hot water switch is turned on (the heat pump is making hot water or in hot water standby mode), the hot water circulation pump starts to work, lasts for ST34 time, stops working and lasts for the time set by ST33, then starts working again and lasts for ST34 time, and so on.

## Vacation
1） Holiday Mode Activation (Switch) Allows the heat pump to operate in holiday mode. 2） Holiday Mode Start Time Configuration Sets the start time for holiday mode. 3） Holiday Mode End Time Configuration Sets the end time for holiday mode. 4） Scheduled Startup Configuration If scheduled startup is enabled, the heat pump will automatically resume operation before the end of holiday mode to ensure sufficient heating and hot water supply. 5） Heating Target Temperature Reduction Adjusts the heating target temperature by a preset reduction value when temperature reduction mode is enabled. 6）Cooling Target Temperature Increase Adjusts the cooling target temperature by a preset increase value when temperature reduction mode is enabled. 7） Hot Water Target Temperature Reduction Adjusts the hot water target temperature by a preset reduction value when temperature reduction mode is enabled.

## Anti-Legionella
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
| Sterilization function switch |  |  |  |  | Sterilization function switch
| Longest sterilization time |  |  |  |  | Reserved parameters
ST26 | Hot water sterilization interval | 360 | 0 | 1000 | H | Sterilization interval
ST27 | Hot water sterilization temperature setting value | 65 | 55 | 70 | ℃ | No need to modify parameters

## Auxiliary heater
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
User Parameters
ST07 | Start air conditioning electric heating outdoor temperature set point | 0 | -10 | 20 | ℃ | No setup required
ST200 | Start boiler external temperature setting | 0 | -25 | 20 | ℃ | No setup required
ST201 | Boiler replaces compressor working external temperature setting | -15 | -30 | 20 | ℃ | No setup required
SF225 | Air conditioning electric heating power setting | 3 | 0 | 9 | KW | No setup required
SF226 | Hot water electric heating power setting | 2.5 | 0 | 9 | KW | No setup required
DF15 | Outdoor temperature to start defrosting electric heating | 0 | -10 | 10 | ℃ | No setup required
PF104 | Defrost electric heating power setting | 0 | 0 | 1000 | wh | Reserved parameters
Control switch
SF112 | Manual electric heating function/air conditioning electric heating configuration selection | 0 (off) | 0 (off) | 1 (on) | - | Configure according to actual installation situation
SF224 | Boiler switching function | 0 (off) | 0 (off) | 1 (on) | - | Configure according to the actual installation situation
SF114 | Hot water electric heating configuration selection | 0 (none) | 0 (none) | 1 (yes) | - | Configure according to the actual installation situation

## Solar
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
User Parameters
ST72 | Solar heating upper limit temperature | 70 | 40 | 90 | ℃ | No setup required
ST73 | Solar pipe antifreeze function starts external temperature setting parameters | 2 | -20 | 10 | ℃ | No setup required
SF301 | Solar function startup parameters | 0 (off) | 0 (off) | 1 (on) | - | Select according to actual application
SF302 | Solar energy application parameters | 0(solar heating) | 0(solar heating) | 1(Solar water heating) | - | Select according to actual application
ST70 | Solar water pump start setting value | 20 | 10 | 40 | ℃ | No setup required
ST71 | Solar water pump shut-off temperature difference set value | 5 | 0 | 10 | ℃ | No setup required
SF304 | Solar pipeline antifreeze water pump stop time parameters | 30 | 30 | 120 | Min. | No setup required

## status
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
Run parameters
RT_Temp_IO | Indoor return water temperature | - | - | - | ℃
ST_Temp | Indoor water outlet temperature | - | - | - | ℃
OT_Temp | Outdoor temperature | - | - | - | ℃
ET_Temp | Return air temperature | - | - | - | ℃
PT_Temp | Exhaust temperature | - | - | - | ℃
LPS | Low pressure | - | - | - | bar.
HPS | High pressure | - | - | - | bar.
Water_Flw | Pump flow feedback | - | - | - | m³/h
LPS_Temp | Evaporation temperature | - | - | - | ℃
HPS_Temp | Condensation temperature | - | - | - | ℃
EEV | Electronic expansion valve opening | - | - | - | -
SuperHeat | Current superheat of the unit | - | - | - | ℃
Comp_Freq | Compressor operating frequency | - | - | - | Hz
Pump_Perc | Pump output percentage | - | - | - | %
Fan_Valve | Fan voltage | - | - | - | V
Version | Program Version | - | - | - | -
HT_Temp | Hot water temperature | - | - | - | ℃
Comp_Time | Compressor running time | - | - | - | H
| Actual target temperature in current mode | - | - | - | ℃
Unit_State | Host Status | - | - | - | -
Comp_current | Compressor current | - | - | - | A
AC current | Input current | - | - | - | A
Comp_power | Compressor power | - | - | - | W
EEV2_Step | EEV2 steps | - | - | - | -
EEV2_SH | EEV2 superheat | - | - | - | ℃
Comp_Freq_Order | Compressor frequency command | - | - | - | -
IPM_Temp | Driver board IPM temperature | - | - | - | ℃
DI_BITS | DI status DI6: SG1 (bit 0), DI7: SG2 (bit 1), boiler status (bit 3), DI mode input status (bit 4, displayed only when the mode input function is enabled) | - | - | - | -
FAN_Speed_1 | Fan 1 feedback speed | - | - | - | rpm/min
FAN_Speed_2 | Fan 2 feedback speed | - | - | - | rpm/min
WIFI_STATUS | Tuya Wi-Fi status | - | - | - | -
IB3 | IO Board B3: Solar Temperature | - | - | - | ℃
IB4 | IO board B4: low temperature zone mixed water temperature | - | - | - | ℃
IB5 | IO board B5: mixed water temperature in high temperature area | - | - | - | ℃
IY2 | IO board Y2: zone proportional water valve opening | - | - | - | %
RT_Temp | ViewSonic motherboard return water temperature | - | - | - | ℃
Comp | bit0: compressor running | - | - | - | -
Pump | bit1: Indoor water pump running | - | - | - | -
Fan | bit2: Outdoor fan running | - | - | - | -
DI5 | bit3:DI5 hot water switch | - | - | - | -
DI4 | bit4: DI4 air conditioner start | - | - | - | -
4_Way_Valve | bit5: four-way valve | - | - | - | -
AC_Heater | bit6: auxiliary electric heating | - | - | - | -
Crankshaft_Heater | bit7: Crankshaft electric heating | - | - | - | -
HT_Pump | bit8: hot water circulation pump | - | - | - | -
3_Way_Valve | bit9: hot water three-way valve | - | - | - | -
HT_Heater | bit10: Electric heating of hot water | - | - | - | -
Def_Heater | bit11: defrost electric heating | - | - | - | -
DI3_IO | bit13: IO board: DI3 low temperature zone control signal | - | - | - | -
DI4_IO | bit14: IO board: DI4 high temperature zone control signal | - | - | - | -
TYNSB | bit15:IO board: solar water pump status | - | - | - | -
FQSB | bit1: IO board: partition water pump status | - | - | - | -
WFS | bit2: Water flow switch/power lock status | - | - | - | -
HVS1 | bit3: high voltage switch | - | - | - | -
| bit4: SF37 unit fault signal output point status | - | - | - | -
| bit5: SF37 unit operation mode output point status | - | - | - | -
| bit6: SF37 mixing valve open signal status | - | - | - | -
| bit7: SF38 unit power on/off signal output status | - | - | - | -
| bit8: SF39 unit operation mode output point status | - | - | - | -
| bit9: SF39 mixing valve closing signal status | - | - | - | -

## Alarm
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
Alarm point
AL01 | Low voltage protection alarm | - | - | - | -
AL02 | High voltage protection alarm | - | - | - | -
AL03 | Indoor low outlet water temperature protection | - | - | - | -
AL04 | Outdoor low outlet water temperature protection | - | - | - | -
AL05 | Indoor high outlet water temperature protection | - | - | - | -
AL17 | Indoor water flow protection alarm | - | - | - | -
AL18 | 24-hour low voltage protection alarm when the number of times exceeds the specified value | - | - | - | -
AL19 | 24-hour high-voltage protection alarm when the number of times exceeds the specified value | - | - | - | -
AL20 | Low evaporation temperature protection alarm | - | - | - | -
AL21 | Exhaust temperature protection alarm | - | - | - | -
AL31 | 24-hour low evaporation temperature protection alarm when the number of times exceeds the specified value | - | - | - | -
AL30 | Communication failure between the main control board and the IO board 3.0 | - | - | - | -
AL37 | Low pressure sensor fault alarm | - | - | - | -
AL38 | High pressure sensor fault alarm | - | - | - | -
AL71 | B1 water inlet temperature sensor fault alarm | - | - | - | -
AL72 | B2 water outlet temperature sensor fault alarm | - | - | - | -
AL73 | B3 ambient temperature sensor fault alarm | - | - | - | -
AL74 | B4 hot water temperature sensor fault alarm | - | - | - | -
AL75 | B5 exhaust temperature sensor fault alarm | - | - | - | -
AL76 | B8 return air temperature sensor fault alarm | - | - | - | -
AL79 | Abnormal water pump duty cycle | - | - | - | -
AL98 | Compressor variable frequency drive board fault alarm | - | - | - | -
AL57 | Communication failure between the main control board and the driver board | - | - | - | -
WN01 | Indoor pipeline antifreeze protection alarm | - | - | - | -
ALEP | Main control board memory EPROM failure | - | - | - | -
AL100 | IPM overcurrent | - | - | - | -
AL101 | Compressor drive failure | - | - | - | -
AL102 | Compressor overcurrent | - | - | - | -
AL103 | Input voltage phase loss | - | - | - | -
AL104 | IPM current sampling fault | - | - | - | -
AL105 | Radiator overheating shutdown | - | - | - | -
AL106 | Precharge failure | - | - | - | -
AL107 | DC bus overvoltage | - | - | - | -
AL108 | DC bus undervoltage | - | - | - | -
AL109 | AC input undervoltage | - | - | - | -
AL110 | AC input overcurrent | - | - | - | -
AL111 | Input voltage sampling failure | - | - | - | -
AL112 | DC fan 1 fault | - | - | - | -
AL113 | Temperature sensor failure | - | - | - | -
AL114 | DC fan 2 fault | - | - | - | -
AL115 | Communication with the main control board is abnormal | - | - | - | -
AL00 | Communication failure between the main control board and the screen | - | - | - | -
AL202 | IO Board: Solar Temperature Sensor Failure | - | - | - | -
AL203 | IO board: Low temperature partition B4 temperature sensor failure | - | - | - | -
AL204 | IO board: High temperature partition B5 temperature sensor failure | - | - | - | -
AL133 | IPM module overheating shutdown | - | - | - | -
AL134 | Compressor model failure | - | - | - | -
AL77 | External coil temperature sensor fault alarm | - | - | - | -
AL22 | High voltage switch fault alarm | - | - | - | -
AL39 | The 24h high voltage switch fault alarm exceeds the specified number of times | - | - | - | -

## Service
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
User Parameters
ST12 | Cooling maximum set point | 30 | 12 | 40 | ℃ | No setup required
ST13 | Heating minimum set point | 20 | 0 | 50 | ℃ | No setup required
ST15 | Minimum domestic hot water setting point | 20 | 0 | 65 | ℃ | No setup required
Condensers
CN01 | EC fan operating upper limit | 4.2 | 2.8 | 10 | V | No setup required
CN02 | EC fan operating lower limit | 3.1 | 1 | 4.2 | V | No setup required
Evaporator parameters
EV14 | Cooling target superheat | 15 | 0 | 20 | ℃ | No setup required
EV15 | Heating target superheat | 12 | 0 | 20 | ℃ | No setup required
Compressor parameters
CM12 | Maximum cooling frequency | 90 | 20 | 120 | Hz | No setup required
CM15 | Maximum heating frequency | 90 | 20 | 120 | Hz | No setup required
CM17 | Hot water maximum frequency | 90 | 20 | 120 | Hz | No setup required
SF05 | Hot water function | 0 (off) | 0 (off) | 1 (on) | - | Select according to actual application: 1. If the heat pump hot water function is used and the pipes are correctly connected, it can be turned on; 2. If the heat pump hot water function is not used, please turn it off;
SF13 | Hot water switch selection | 1(Screen switch) | 0 (DI switch) | 1(Screen switch) | - | Select according to the actual application: 1. If you use a touch screen to control the hot water on/off, please select "Screen"; 2. If you use a DI signal to control the hot water on/off, please select "DI";
SF14 | Air conditioner power on/off selection | 1(Screen switch) | 0 (DI switch) | 1(Screen switch) | - | Select according to actual application: 1. If you use a touch screen to control the H/C on/off, please select "Screen"; 2. If you use a DI signal to control the H/C on/off, please select "DI";
DF04 | Defrost temperature difference (OT-LPS corresponding) set point | 8 | 8 | 20 | ℃ | No setup required
EV07 | Refrigeration/defrosting water pump flow feedback protection value | 0.9 | 0 | 9.9 | m³/h | No setup required
EV25 | Hot water pump feedback flow protection value | 0.5 | 0 | 9.9 | m³/h | No setup required
SF37 | Hot water circulation pump output selection | Hot water circulation pump | 1 | 4 | -
SF38 | Hot water electric heating output selection | Hot water electric heating | 1 | 2 | - | You can select the corresponding function options according to the actual application;
SF39 | Unit operation mode output selection | Unit operating mode | 1 | 3 | - | You can select the corresponding function options according to the actual application;
Parameter code | Corresponding output port (without IO board) | The corresponding output port is not equipped with an IO board | Function options
SF37 | 3-phase power supply heat pump: OUT9; Single-phase power supply heat pump: OUT8; | IO board output port: NO3 | 1: Hot water circulation pump control logic output point; 2: Unit fault signal output point; 3: Unit operation mode output point; 4: Three-point mixing valve switch signal output point;
SF38 | 3-phase power supply heat pump:OUT6; Single-phase power supply heat pump:OUT6; | IO board output port: KA2 | 1: Hot water electric heating control logic output point; 2: Unit power on/off signal output point;
SF39 | - | IO board output port: NO5 | 1: Unit operation mode output point; 2: Solar water pump output point; 3: Three-point mixing valve switch signal output point;

## manufacturer
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
User Parameters
CN21 | Maximum fan speed | 800 | 20 | 1200 | rpm/min | No setup required
CN20 | Minimum fan speed | 300 | 20 | 600 | rpm/min | No setup required
SF215 | Compressor code | 76 | 0 | 999 | - | Select the corresponding number according to the model in the table below
SF200 | Expansion board function | 0 (without) | 0 (without) | 1(belt) | - | Select the configuration according to the actual application: 1. If you are configuring an indoor unit control box/hydraulic module/hydraulic tower, please select Open; 2. If you are not configuring an indoor unit, please select Close;
DF06 | Minimum defrost interval | 30 | 15 | 90 | Min. | No setup required
DF16 | Forced defrost operation time | 180 | 120 | 180 | Min. | No setup required
AR03 | High outlet water temperature protection value | 77 | 1 | 100 | ℃ | No setup required
AR08 | Low evaporation temperature protection value | -2 | -10 | 10 | ℃ | No setup required
SF201 | Power lock function switch | 0 (off) | 0 (off) | 1 (on) | - | If you need to use it, please ask after-sales staff
SF221 | Current limiting function | 0 (off) | 0 (off) | 1 (on) | - | No setup required
SF48 | Manual defrost function | 0 (off) | 0 (off) | 1 (on) | - | If manual defrosting is required, please turn on the manual defrost function; the heat pump will automatically enter the defrost operation and the switch will automatically reset after 5 seconds;
SF222 | Cancel the forced defrost function | 0 (off) | 0 (off) | 1 (on) | - | No setup required
SF219 | Displays cumulative heat generation and power consumption | 0 (not displayed) | 0 (not displayed) | 1 (display) | - | No setup required
SF113 | DI input mode selection function | 0 (off) | 0 (off) | 1 (on) | - | If you need to use DI input signal to select the unit mode, please select "ON";
SF224 | Boiler switching function | 0 (off) | 0 (off) | 1 (on) | - | No setup required
SF56 | Accumulated heat generation and accumulated power consumption are reset to zero | 0 (do not clear) | 0 (do not clear) | 1 (clear) | - | Used when the accumulated values of heat pump heat production and power consumption need to be cleared;
Appendix 1:

## Pump set
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
ST60 | Refrigeration outlet and return water temperature difference setting value | 5 | 0 | 10 | ℃ | No setup required
ST61 | Heating outlet and return water temperature difference setting value | 5 | 0 | 10 | ℃ | No setup required
SF35 | Water pump model selection | HBGF 25-80-130 | 1 | 1000 | - | Set according to the pump model in the list
EV05 | Water pump PWM upper limit | 100 | 10 | 100 | - | No setup required
EV06 | Water pump PWM lower limit | 70 | 10 | 100 | - | No setup required
PF102 | Pump rated power setting | 90 | 10 | 200 | wh | No setup required
SF10 | Water pump configuration | 0 (external) | 0 (external) | 1 (built-in) | - | Set the water pump according to its actual installation location: 1. If the water pump is installed in the heat pump, select "Built-in"; 2. If the water pump is installed outside the heat pump (when installed in a hydraulic module or hydraulic tower), select "External";
EV01 | Pump operation mode | 0 (continuous operation) | 0 (continuous operation) | 1 (auto start/stop) | - | No setup required
SF46 | Water flow fault shielding switch | 0 (off) | 0 (off) | 1 (on) | - | No setup required
Water pump model | Heat pump model | Heat pump classification
UPM3K | CHS06V | Chiller
CHS10V
UPML/UPMXL | CHS15V
UPMF20-125-PCI | CHS22V
HBGF 25-80-130 | HS06V | Heatpump
HS08V
HS10V
HS12V
HBF 25-105-130 | HS15V
HBGF25-125-130 | HS22V
other | - | -
When the user chooses to connect an external water pump, he can select the "other" water pump type, and the unit will detect the system water flow signal in the form of a water flow switch;

## SGready
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
SF217 | SG function | 0（Off） | 0（Off） | 1（On） | - | Select by actual application
ST17 | SG function cooling or heating temperature range | 2 | 1 | 10 | ℃ | No setup required
ST18 | SG function hot water temperature range | 5 | 1 | 10 | ℃ | No setup required

## Test mode
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | Unit
SF223 | Debug Mode | 0 (off) | 0 (off) | 1 (on) | - | Debug mode switch
Water_Flw | Pump flow feedback | - | - | - | m³/h
Pump_Perc | Pump output percentage | - | - | - | %
1. After the first installation of the heat pump is completed and the system needs to be vented, the debug mode can be used: 1) After turning on the debug mode switch, the unit will automatically run the water pump to circulate and vent the water in the system and display the real-time water flow value; 2) After the venting is completed, turn off the debug mode switch and the heat pump will exit the debug mode;

## installation
name | Component 1 | Component 2 | Component 3 | 1. Select the configuration according to the actual installation situation on site; after selecting the correct configuration, the touch screen home page will change accordingly;
Indoor unit | Hydraulic tower | Control center/hydraulic module | -
Buffer water tank | Buffer water tank | - | -
Auxiliary heat source | boiler | - | -
Heating terminal | Radiator | Floor heating | fan coil units
Solar energy applications | Solar cooling and heating | Solar water heating | -

## System
1. System time settings. After configuring and connecting to Wi-Fi, the system time will automatically calibrate. 2. Touch screen off timer settings. 3. Touch screen brightness settings. 4. System language settings.

## ALL
Dentwiton Export Unit Agreement
Version: CJ4.1 Date: May 13, 2025
Code | Content | Default Value | Minimum | Maximum | unit | Accuracy | address | Permissions | Remark
用户参数
Mode | Mode Switching | 2（Cooling) | 1（heating) | 2(Cooling) | - | 1 | 4X0001 | 0 | WIFI upload screen display
ST01 | Cooling mode set point | 13 | ST11 | ST12 | ℃ | 0.1 | 4X0002 | 0 | WIFI upload screen display
ST02 | Heating mode set point | 40 | ST13 | ST14 | ℃ | 0.1 | 4X0003 | 0 | WIFI upload screen display
ST03 | Adjustable temperature range in cooling mode | 2 | 1 | 10 | ℃ | 0.1 | 4X0004 | 1
ST04 | Adjustable temperature range in heating mode | 2 | 1 | 10 | ℃ | 0.1 | 4X0005 | 1
ST06 | Heating climate compensation coefficient | 0.6 | 0 | 3 | ℃ | 0.1 | 4X0006 | 1
ST07 | Start air conditioning electric heating outdoor temperature set point | 0 | -10 | 20 | ℃ | 0.1 | 4X0007 | 1
ST08 | Refrigeration climate compensation factor | 0.6 | 0 | 3 | ℃ | 0.1 | 4X0008 | 1
ST09 | Domestic hot water temperature set point | 50 | 20 | 75 | ℃ | 0.1 | 4X0009 | 0
ST10 | Domestic hot water temperature range | 5 | 1 | 10 | ℃ | 0.1 | 4X0010 | 1
ST11 | Cooling minimum set point | 12 | 0 | 40 | ℃ | 0.1 | 4X0011 | 1
ST12 | Cooling maximum set point | 30 | 12 | 40 | ℃ | 0.1 | 4X0012 | 0
ST13 | Heating minimum set point | 20 | 0 | 50 | ℃ | 0.1 | 4X0013 | 1
ST14 | Heating maximum setting point | 65 | 20 | 80 | ℃ | 0.1 | 4X0014 | 0
ST15 | Minimum domestic hot water setting point | 20 | 0 | 65 | ℃ | 0.1 | 4X0015 | 2
ST16 | Domestic hot water maximum setting point | 70 | 20 | 80 | ℃ | 0.1 | 4X0016 | 2
ST17 | SG function cooling or heating temperature range | 2 | 1 | 10 | ℃ | 0.1 | 4X0017 | 0
ST18 | SG function hot water temperature range | 5 | 1 | 10 | ℃ | 0.1 | 4X0018 | 0
ST26 | Hot water sterilization interval | 360 | 0 | 1000 | H | 1 | 4X0020 | 1
ST27 | Hot water sterilization temperature setting value | 65 | 55 | 70 | ℃ | 0.1 | 4X0021 | 2
ST33 | Hot water circulation pump interval time | 15 | 0 | 180 | Min. | 1 | 4X0022 | 0
ST34 | Hot water circulation pump operating time | 3 | 0 | 180 | Min. | 1 | 4X0023 | 0
ST60 | Refrigeration outlet and return water temperature difference setting value | 5 | 0 | 10 | ℃ | 0.1 | 4X0024 | 2 | Display
ST61 | Heating outlet and return water temperature difference setting value | 5 | 0 | 10 | ℃ | 0.1 | 4X0025 | 2 | Display
ST72 | Solar heating upper limit temperature | 70 | 40 | 90 | ℃ | 0.1 | 4X0026 | 0
ST73 | Solar pipe antifreeze function starts external temperature setting parameters | 2 | -20 | 10 | ℃ | 0.1 | 4X0027 | 0
ST37 | Discharge temperature setpoint minus target superheat 1 | 95 | 60 | 120 | ℃ | 0.1 | 4X0036 | 2
ST35 | Discharge temperature setpoint minus target superheat 2 | 97 | 60 | 120 | ℃ | 0.1 | 4X0037 | 2
ST38 | Discharge temperature setpoint minus target superheat 3 | 99 | 60 | 120 | ℃ | 0.1 | 4X0038 | 2
ST103 | IPM module temperature protection value | 90 | 60 | 120 | ℃ | 0.1 | 4X0039 | 1
ST200 | Start boiler external temperature setting | 0 | -25 | 20 | ℃ | 0.1 | 4X0040 | 0
ST201 | Boiler replaces compressor working external temperature setting | -15 | -30 | 20 | ℃ | 0.1 | 4X0041 | 2
ST02H | High temperature zone target set temperature (heating set temperature) | 55 | 20 | 60 | ℃ | 0.1 | 4X0042 | 2
ST01H | High temperature zone target set temperature (cooling set temperature) | 18 | 12 | 40 | ℃ | 0.1 | 4X0043 | 2
ST06H | High temperature zone heating temperature compensation coefficient | 0.6 | 0 | 2 | - | 0.1 | 4X0044 | 2
ST08H | High temperature area refrigeration temperature compensation coefficient | 0.6 | 0 | 2 | - | 0.1 | 4X0045 | 2
ST02L | Low temperature zone target set temperature (heating set temperature) | 35 | 20 | 60 | ℃ | 0.1 | 4X0046 | 2
ST01L | Low temperature zone target set temperature (cooling set temperature) | 18 | 12 | 40 | ℃ | 0.1 | 4X0047 | 2
ST06L | Low temperature zone heating temperature compensation coefficient | 0.6 | 0 | 2 | ℃ | 1 | 4X0048 | 2
ST08L | Low temperature zone refrigeration temperature compensation coefficient | 0.6 | 0 | 2 | ℃ | 1 | 4X0049 | 2
SF04H | High temperature area temperature compensation function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 4X0050 | 2
SF04L | Low temperature area temperature compensation function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 4X0051 | 2
ST118 | Hot water temperature sensor compensation value | 0 | -10 | 10 | ℃ | 0.1 | 4X0052 | 2
Condensers
CN01 | EC fan operating upper limit | 4.2 | 2.8 | 10 | V | 0.1 | 4X0100 | 1 | WIFI upload screen display
CN02 | EC fan operating lower limit | 3.1 | 1 | 4.2 | V | 0.1 | 4X0101 | 1
CN03 | Refrigeration condensing pressure lower limit | 15 | 2 | 20 | bar. | 0.1 | 4X0102 | 0
CN04 | Refrigeration condensing pressure upper limit | 9 | 2 | 50 | bar. | 0.1 | 4X0103 | 2
CN05 | Heating evaporation temperature lower limit | 3.5 | 2 | 20 | bar. | 0.1 | 4X0104 | 2
CN06 | Heating evaporation temperature upper limit | 4.5 | 2 | 20 | bar. | 0.1 | 4X0105 | 2
CN200 | Night mode fan maximum speed | 660 | 300 | 900 | rpm/min | 1 | 4X0108 | 1
CN21 | Maximum fan speed | 800 | 20 | 1200 | rpm/min | 1 | 4X0109 | 2
CN20 | Minimum fan speed | 300 | 20 | 600 | rpm/min | 1 | 4X0110 | 2
Evaporator parameters
EV12 | Initial cooling opening | 480 | 10 | 480 | - | 1 | 4X0152 | 2
EV14 | Cooling target superheat | 15 | 0 | 20 | ℃ | 0.1 | 4X0153 | 1
EV15 | Heating target superheat | 12 | 0 | 20 | ℃ | 0.1 | 4X0154 | 1
Compressor parameters
CM02 | Compressor shutdown and restart time | 180 | 1 | 1000 | Sec. | 1 | 4X0200 | 2
CM12 | Maximum cooling frequency | 90 | 20 | 120 | Hz | 1 | 4X0201 | 1 | Display
CM13 | Minimum cooling frequency | 30 | 20 | 60 | Hz | 1 | 4X0202 | 2
CM15 | Maximum heating frequency | 90 | 20 | 120 | Hz | 1 | 4X0203 | 1 | Display
CM16 | Minimum heating frequency | 30 | 20 | 60 | Hz | 1 | 4X0204 | 2
CM17 | Hot water maximum frequency | 90 | 20 | 120 | Hz | 1 | 4X0205 | 1
CM18 | Minimum frequency of hot water | 40 | 20 | 60 | Hz | 1 | 4X0206 | 2
CM30 | Minimum frequency at low temperatures | 50 | 20 | 80 | Hz | 1 | 4X0211 | 2
CM200 | Night mode maximum frequency | 70 | 20 | 90 | Hz | 1 | 4X0212 | 1
SF85 | Enter the current limit setting value | 21 | 0.5 | 80 | A | 0.1 | 4X0213 | 2
SF86 | Exit current limit setting value | 16 | 0.5 | 80 | A | 0.1 | 4X0214 | 2
SF65 | Compression ratio | 15 | 0 | 50 | - | 0.1 | 4X0215 | 2
SF215 | Compressor code | 76 | 0 | 999 | - | 1 | 4X0224 | 2 | See Appendix 1 for specific models
P33 | Exhaust superheat target value | 40 | 20 | 60 | ℃ | 0.1 | 4X0225 | 2
CM10 | Minimum defrost frequency (defrost four-way valve switching frequency) | 45 | 20 | 120 | Hz | 1 | 4X0232 | 1
CM11 | Refrigeration rated frequency | 85 | 20 | 120 | Hz | 1 | 4x0233 | 2
CM14 | Heating rated frequency | 85 | 20 | 120 | Hz | 1 | 4x0234 | 2
Electronic expansion valve parameters
SF31 | Manually set the EEV1 opening | 200 | 0 | 480 | - | 1 | 4X0250 | 2
SF32 | Manually set the EEV2 opening | 200 | 0 | 480 | - | 1 | 4X0251 | 2
SF51 | EEV minimum opening | 50 | 0 | 150 |  | 1 | 4X0252 | 2
SF83 | PID adjustment cycle of EEV | 10 | 0 | 20 | - | 1 | 4X0253 | 2
SF28 | PID regulation Kp of EEV cooling | 3 | 2 | 600 | - | 1 | 4X0254 | 2
SF29 | PID Regulation of EEV Refrigeration | 80 | 0 | 1000 | - | 1 | 4X0255 | 2
SF30 | PID regulation Td of EEV cooling | 2 | 0 | 100 | - | 1 | 4X0256 | 2
SF115 | When heating, the EEV initial opening degree is when the outside temperature is -10℃ to 0℃ | 160 | 0 | 480 | - | 1 | 4X0257 | 2
SF116 | When heating, the EEV initial opening is when the outside temperature is less than -10℃ | 120 | 0 | 480 | - | 1 | 4X0258 | 2
SF212 | When heating, the EEV initial opening degree is when the outside temperature is greater than 20℃ | 430 | 0 | 480 | - | 1 | 4X0259 | 2
SF213 | EEV initial opening when outside temperature is 0℃ to 10℃ during heating | 280 | 0 | 480 | - | 1 | 4X0260 | 2
SF214 | When heating, the EEV initial opening degree is when the outside temperature is 10℃ to 20℃ | 360 | 0 | 480 | - | 1 | 4X0261 | 2
Special parameters
SF04 | Temperature compensation function activated | 0 (off) | 0 (off) | 1 (on) | - | 1 | 4X0300 | 1
SF05 | Hot water function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 4X0301 | 0
SF06 | Antifreeze start outdoor temperature | 2 | 0 | 10 | ℃ | 1 | 4X0302 | 2
SF08 | Antifreeze start return water temperature | 10 | 1 | 20 | ℃ | 0.1 | 4X0303 | 2
SF09 | Return water temperature range after antifreeze ends | 2 | 1 | 10 | ℃ | 0.1 | 4X0304 | 2
SF13 | Hot water switch selection | 1(Screen switch) | 0 (DI switch) | 1(Screen switch) | - | 1 | 4X0305 | 0
SF14 | Air conditioner power on/off selection | 1(Screen switch) | 0 (DI switch) | 1(Screen switch) | - | 1 | 4X0306 | 0
SF33 | Manually set the compressor frequency | 70 | 0 | 120 | - | 1 | 4X0307 | 2
SF227 | Outdoor fan rated power | 250 | 10 | 1000 | W | 1 | 4X0308 | 2
SF100 | Exhaust temperature is too high and the frequency reduction protection value | 100 | 80 | 120 | ℃ | 0.1 | 4X0309 | 2
SF211 | Water flow setting | 0 | 0 | 10 | m³/h | 0.1 | 4X0316 | 2
SF225 | Air conditioning electric heating power setting | 3 | 0 | 9 | KW | 0.1 | 4X0317 | 2 | Two levels of selection
SF226 | Hot water electric heating power setting | 2.5 | 0 | 9 | KW | 0.1 | 4X0318 | 2 | Two levels of selection
SF301 | Solar function startup parameters | 0 (off) | 0 (off) | 1 (on) | - | 1 | 4X0319 | 0
SF302 | Solar energy application parameters | 0(solar heating) | 0(solar heating) | 1(Solar water heating) | - | 1 | 4X0320 | 0
SF303 | Zone temperature control function activated | 0 (off) | 0 (off) | 1 (on) |  | 1 | 4X0321 | 2
SF400 | Hot water delay interval function parameters | 1 (on) | 0 (off) | 1 (on) | - | 1 | 4X0322 | 2
SF200 | Expansion board function | 0(belt) | 0 (without) | 1(belt) | - | 1 | 4X0323 | 2
P47 | Refrigerant Type | 0 | 0 | 2 | - | 1 | 4X0324 | 2 | 0 is R290, 1 is 410A, 2 is R32
SF37 | Hot water circulation pump output selection | 1 | 1 | 4 | - | 1 | 4X0326 | 1 | 1 is the hot water circulation pump; 2 is the unit fault signal; 3 is the unit operation mode output; 4 is the three-point mixing valve open signal output
SF38 | Hot water electric heating output selection | 1 | 1 | 2 | - | 2 | 4X0327 | 1 | 1 is hot water electric heating; 2 is the unit on/off signal;
SF39 | Unit operation mode output selection | 1 | 1 | 3 | - | 3 | 4X0328 | 1 | 1 is the unit operation mode output; 2 is the solar water pump; 3 is the three-point mixing valve closing signal output
SF62 | Low voltage distribution power | 100 | 0 | 1000 | wh | 1 | 4X0329 | 2
E.T | Target power consumption | - | - | - | - | - | 4X0330
SF228 | Model confirmation | 0 | 0 | 88 | - | 1 | 4X0335 |  | 0 means the host has been changed; 88 means the host has not been changed
Defrost parameters
DF02 | LPS corresponds to the temperature set point | -2 | -10 | 10 | ℃ | 0.1 | 4X0400 | 1
DF03 | Defrost outdoor temperature set point | 12 | 3 | 20 | ℃ | 0.1 | 4X0401 | 1 | WIFI upload screen display
DF04 | Defrost temperature difference (OT-LPS corresponding) set point | 8 | 8 | 20 | ℃ | 0.1 | 4X0402 | 1
DF05 | Duration when DF04 is met | 60 | 1 | 1000 | Sec. | 1 | 4X0403 | 1
DF06 | Minimum defrost interval | 30 | 15 | 90 | Min. | 1 | 4X0404 | 2
DF09 | HPS corresponding temperature for exiting defrost | 35 | 5 | 60 | ℃ | 0.1 | 4X0405 | 2
DF10 | Maximum defrost time | 480 | 5 | 1000 | Sec. | 1 | 4X0406 | 1
DF11 | Defrost evaporation temperature meets time | 300 | 5 | 3600 | Sec. | 1 | 4X0407 | 1
DF13 | Fan start temperature | 25 | 5 | 60 | ℃ | 0.1 | 4X0408 | 2
DF15 | Outdoor temperature to start defrosting electric heating | 0 | -10 | 10 | ℃ | 0.1 | 4X0409 | 2
DF16 | Forced defrost operation time | 180 | 120 | 180 | Min. | 1 | 4X0410 | 2 | Display
PF104 | Defrost electric heating power setting | 0 | 0 | 1000 | wh | 1 | 4X0411 | 2
DF20 | Return water temperature value for starting the air conditioning pump | 15 | 5 | 25 | ℃ | 0.1 | 4X0412 | 2
Alarm parameters
AR01 | Low outlet water temperature protection value | 5.5 | 1 | 20 | ℃ | 0.1 | 4X0450 | 2 | Display
AR03 | High outlet water temperature protection value | 77 | 1 | 100 | ℃ | 0.1 | 4X0451 | 2
AR04 | Indoor water pump shielding time | 120 | 1 | 120 | Sec. | 1 | 4X0452 | 2
AR06 | Total number of low pressure alarms within 24 hours (alarm AL18 if higher) | 4 | 1 | 20 | - | 1 | 4X0453 | 1
AR07 | Total number of high pressure alarms within 24 hours (higher than AL19) | 6 | 1 | 10 | - | 1 | 4X0454 | 1
AR08 | Low evaporation temperature protection value | -2 | -10 | 10 | ℃ | 0.1 | 4X0455 | 2
AR09 | Low voltage protection shielding time | 300 | 10 | 1000 | Sec. | 1 | 4X0456 | 2
AR13 | High exhaust temperature protection | 105 | 100 | 130 | ℃ | 0.1 | 4X0457 | 2
AR14 | High exhaust temperature protection range | 20 | 1 | 30 | ℃ | 0.1 | 4X0458 | 2
AR16 | Total number of low evaporation temperature protection times within 24 hours | 3 | 1 | 20 | - | 1 | 4X0459 | 1
AR29 | Antifreeze interval | 30 | 1 | 1000 | - | 1 | 4X0460 | 2
AR31 | Low voltage protection set point | 0.3 | 0.1 | 6 | bar. | 0.1 | 4X0461 | 2
AR32 | Low voltage protection range | 0.3 | 0.1 | 6 | bar. | 0.1 | 4X0462 | 2
AR33 | High voltage protection set point | 30 | 25 | 50 | bar. | 0.1 | 4X0463 | 2
AR34 | High voltage protection range | 3 | 1 | 10 | bar. | 0.1 | 4X0464 | 2
AR35 | Outdoor low outlet water temperature protection set point |  | 0 | 20 | ℃ | 0.1 | 4X0465 | 2 | Domestic sales non-high temperature heat pump
AR36 | Outdoor low outlet water temperature protection range |  | 0 | 10 | ℃ | 0.1 | 4X0466 | 2 | Domestic sales non-high temperature heat pump
Pump parameters
SF35 | Water pump model selection | 64 | 1 | 1000 | - | 1 | 4X0500 | 2 | See Appendix 2 for specific models
EV05 | Water pump PWM upper limit | 100 | 10 | 100 | - | 1 | 4X0501 | 1
EV06 | Water pump PWM lower limit | 70 | 10 | 100 | - | 1 | 4X0502 | 1
EV07 | Refrigeration/defrosting water pump flow feedback protection value | 0.9 | 0 | 9.9 | m³/h | 0.1 | 4X0503 | 1 | Display
EV25 | Hot water pump feedback flow protection value | 0.5 | 0 | 9.9 | m³/h | 0.1 | 4X0504 | 1 | Display
ST70 | Solar water pump start setting value | 20 | 10 | 40 | ℃ | 0.1 | 4X0505 | 0
ST71 | Solar water pump shut-off temperature difference set value | 5 | 0 | 10 | ℃ | 0.1 | 4X0506 | 0
SF304 | Solar pipeline antifreeze water pump stop time parameters | 30 | 30 | 120 | Min. | 1 | 4X0507 | 0
PF102 | Pump rated power setting | 90 | 10 | 200 | wh | 1 | 4X0508 | 2
Energy management parameters
SF219 | Cumulative heat production | - | - | - | - | 1 | 4X0550 | 0 | Floating point numbers have high bits first and low bits last
4X0551
Power_Total | Cumulative power consumption | - | - | - | - | 1 | 4X0552 | 0 | Floating point numbers have high bits first and low bits last
4X0553
Run parameters
RT_Temp_IO | Indoor return water temperature | - | - | - | ℃ | 0.1 | 3X0001 | 0
ST_Temp | Indoor water outlet temperature | - | - | - | ℃ | 0.1 | 3X0002 | 0
OT_Temp | Outdoor temperature | - | - | - | ℃ | 0.1 | 3X0003 | 0
ET_Temp | Return air temperature | - | - | - | ℃ | 0.1 | 3X0004 | 0
PT_Temp | Exhaust temperature | - | - | - | ℃ | 0.1 | 3X0005 | 0
LPS | Low pressure | - | - | - | bar. | 0.1 | 3X0006 | 0
HPS | High pressure | - | - | - | bar. | 0.1 | 3X0007 | 0
Water_Flw | Pump flow feedback | - | - | - | m³/h | 0.1 | 3X0008 | 0
LPS_Temp | Evaporation temperature | - | - | - | ℃ | 0.1 | 3X0009 | 0
HPS_Temp | Condensation temperature | - | - | - | ℃ | 0.1 | 3X0010 | 0
EEV | Electronic expansion valve opening | - | - | - | - | 1 | 3X0011 | 0
SuperHeat | Current superheat of the unit | - | - | - | ℃ | 0.1 | 3X0012 | 0
Comp_Freq | Compressor operating frequency | - | - | - | Hz | 1 | 3X0013 | 0
Pump_Perc | Pump output percentage | - | - | - | % | 1 | 3X0014 | 0
Fan_Valve | Fan voltage | - | - | - | V | 0.1 | 3X0015 | 0
Version | Program Version | - | - | - | - | 1 | 3X0016 | 0
HT_Temp | Hot water temperature | - | - | - | ℃ | 0.1 | 3X0017 | 0
Comp_Time | Compressor running time | - | - | - | H | 1 | 3X0018 | 0
| Actual target temperature in current mode | - | - | - | ℃ | 0.1 | 3X0019 | 0
Unit_State | Host Status | - | - | - | - | 1 | 3X0020 | 0
| Room temperature | - | - | - | ℃ | 0.1 | 3X0021 | 0
| Calories | - | - | - | J | 1 | 3X0022 | 0
| Power consumption | - | - | - | WH | 1 | 3X0023 | 0
Comp_current | Compressor current | - | - | - | A | 0.1 | 3X0024 | 0
AC current | Input current | - | - | - | A | 0.1 | 3X0025 | 0
Comp_power | Compressor power | - | - | - | W | 1 | 3X0026 | 0
EEV2_Step | EEV2 steps | - | - | - | - | 1 | 3X0027 | 0
EEV2_SH | EEV2 superheat | - | - | - | ℃ | 0.1 | 3X0028 | 0
Comp_Freq_Order | Compressor frequency command | - | - | - | - | 1 | 3X0029 | 0
IPM_Temp | Driver board IPM temperature | - | - | - | ℃ | 0.1 | 3X0030 | 0
DI_BITS | DI status DI6: SG1 (bit 0), DI7: SG2 (bit 1), boiler status (bit 3), DI mode input status (bit 4, displayed only when the mode input function is enabled) | - | - | - | - | 1 | 3X0031 | 0 | 0: Heating/1: Cooling
FAN_Speed_1 | Fan 1 feedback speed | - | - | - | rpm/min | 1 | 3X0032 | 0
FAN_Speed_2 | Fan 2 feedback speed | - | - | - | rpm/min | 1 | 3X0033 | 0
WIFI_STATUS | Tuya Wi-Fi status | - | - | - | - | 1 | 3X0038 | 0
IB3 | IO Board B3: Solar Temperature | - | - | - | ℃ | 0.1 | 3X0043 | 0
IB4 | IO board B4: low temperature zone mixed water temperature | - | - | - | ℃ | 0.1 | 3X0044 | 0
IB5 | IO board B5: mixed water temperature in high temperature area | - | - | - | ℃ | 0.1 | 3X0045 | 0
IY2 | IO board Y2: zone proportional water valve opening | - | - | - | % | 1 | 3X0046 | 0
RT_Temp | ViewSonic motherboard return water temperature | - | - | - | ℃ | 0.1 | 3X0047 | 0
Comp | bit0: compressor running | - | - | - | - | 1 | 3X0048 | 0
Pump | bit1: Indoor water pump running | - | - | - | - | 1 |  | 0
Fan | bit2: Outdoor fan running | - | - | - | - | 1 |  | 0
DI5 | bit3:DI5 hot water switch | - | - | - | - | 1 |  | 0
DI4 | bit4: DI4 air conditioner start | - | - | - | - | 1 |  | 0
4_Way_Valve | bit5: four-way valve | - | - | - | - | 1 |  | 0
AC_Heater | bit6: auxiliary electric heating | - | - | - | - | 1 |  | 0
Crankshaft_Heater | bit7: Crankshaft electric heating | - | - | - | - | 1 |  | 0
HT_Pump | bit8: hot water circulation pump | - | - | - | - | 1 |  | 0
3_Way_Valve | bit9: hot water three-way valve | - | - | - | - | 1 |  | 0
HT_Heater | bit10: Electric heating of hot water | - | - | - | - | 1 |  | 0
Def_Heater | bit11: defrost electric heating | - | - | - | - | 1 |  | 0
EVI | bit12: enthalpy increase solenoid valve | - | - | - | - | 1 |  | 0
DI3_IO | bit13: IO board: DI3 low temperature zone control signal | - | - | - | - | 1 |  | 0
DI4_IO | bit14: IO board: DI4 high temperature zone control signal | - | - | - | - | 1 |  | 0
TYNSB | bit15:IO board: solar water pump status | - | - | - | - | 1 |  | 0
FQSB | bit1: IO board: partition water pump status | - | - | - | - | 1 | 3X0049 | 0
WFS | bit2: Water flow switch/power lock status | - | - | - | - | 1 |  | 0
HVS1 | bit3: high voltage switch | - | - | - | - | 1 |  | 0 | 0:Disconnect/1:Connect
| bit4: SF37 unit fault signal output point status | - | - | - | - | 1 |  | 0
| bit5: SF37 unit operation mode output point status | - | - | - | - | 1 |  | 0
| bit6: SF37 mixing valve open signal status | - | - | - | - | 1 |  | 0
| bit7: SF38 unit power on/off signal output status | - | - | - | - | 1 |  | 0
| bit8: SF39 unit operation mode output point status | - | - | - | - | 1 |  | 0
| bit9: SF39 mixing valve closing signal status | - | - | - | - | 1 |  | 0
OTC | External coil temperature | - | - | - | ℃ | 0.1 | 3X0099 | 0
ET_Temp_2 | Return air temperature 2 | - | - | - | ℃ | 0.1 | 3X0100 | 0 | System 2
PT_Temp_2 | Exhaust temperature 2 | - | - | - | ℃ | 0.1 | 3X0101 | 0
LPS_2 | Low pressure 2 | - | - | - | bar. | 0.1 | 3X0102 | 0
LPS_Temp_2 | Evaporation temperature 2 | - | - | - | ℃ | 0.1 | 3X0103 | 0
SuperHeat_2 | Current superheat of the unit 2 | - | - | - | ℃ | 0.1 | 3X0104 | 0
Comp_Freq_2 | Compressor operating frequency 2 | - | - | - | Hz | 1 | 3X0105 | 0
Comp_current_2 | Compressor current 2 | - | - | - | A | 0.1 | 3X0106 | 0
AC current_2 | Input current 2 | - | - | - | A | 0.1 | 3X0107 | 0
Comp_power_2 | Compressor power 2 | - | - | - | W | 1 | 3X0108 | 0
Comp_Freq_Order_2 | Compressor frequency command 2 | - | - | - | - | 1 | 3X0109 | 0
Comp_Time_2 | Compressor running time 2 | - | - | - | H | 1 | 3X0110 | 0
OTC_2 | External coil temperature 2 | - | - | - | ℃ | 0.1 | 3X0111 | 0
Unit_State_2 | Host Status_2 | - | - | - | - | 1 | 3X0112 | 0
Fan_Valve_2 | Fan voltage 2 | - | - | - | V | 0.1 | 3X0113 | 0
Crankshaft_Heater_2 | bit0: crankshaft electric heating 2 | - | - | - | - | 1 | 3X0114 | 0
HVS2 | bit1: high voltage switch 2 | - | - | - | - | 1 |  | 0
4_Way_Valve_2 | bit2: four-way valve 2 | - | - | - | - | 1 |  | 0
IPM_Temp_2 | Driver board IPM temperature 2 | - | - | - | ℃ | 0.1 | 3X0115 | 0
Alarm point
AL01 | Low voltage protection alarm | - | - | - | - | 1 | 1x0001 | 0 | WIFI upload
AL02 | High voltage protection alarm | - | - | - | - | 1 | 1x0002 | 0 | WIFI upload
AL03 | Indoor low water protection | - | - | - | - | 1 | 1x0003 | 0 | WIFI upload
AL04 | Outdoor low water outlet temperature protection | - | - | - | - | 1 | 1x0004 | 0 | WIFI upload
AL05 | Indoor high water protection | - | - | - | - | 1 | 1x0005 | 0 | WIFI upload
AL17 | Indoor water flow protection alarm | - | - | - | - | 1 | 1x0006 | 0 | WIFI upload
AL18 | 24-hour low voltage protection alarm when the number of times exceeds the specified value | - | - | - | - | 1 | 1x0007 | 0 | WIFI upload
AL19 | 24-hour high-voltage protection alarm when the number of times exceeds the specified value | - | - | - | - | 1 | 1x0008 | 0 | WIFI upload
AL20 | Low evaporation temperature protection alarm | - | - | - | - | 1 | 1x0009 | 0 | WIFI upload
AL21 | Exhaust temperature protection alarm | - | - | - | - | 1 | 1x0010 | 0 | WIFI upload
AL31 | 24-hour low evaporation temperature protection alarm when the number of times exceeds the specified value | - | - | - | - | 1 | 1x0011 | 0 | WIFI upload
AL30 | Communication failure between the main control board and the IO board 3.0 | - | - | - | - | 1 | 1x0012 | 0 | WIFI upload
AL37 | Low pressure sensor fault alarm | - | - | - | - | 1 | 1x0013 | 0 | WIFI upload
AL38 | High pressure sensor fault alarm | - | - | - | - | 1 | 1x0014 | 0 | WIFI upload
AL71 | B1 water inlet temperature sensor fault alarm | - | - | - | - | 1 | 1x0015 | 0 | WIFI upload
AL72 | B2 water outlet temperature sensor fault alarm | - | - | - | - | 1 | 1x0016 | 0 | WIFI upload
AL73 | B3 ambient temperature sensor fault alarm | - | - | - | - | 1 | 1x0017 | 0 | WIFI upload
AL74 | B4 hot water temperature sensor fault alarm | - | - | - | - | 1 | 1x0018 | 0 | WIFI upload
AL75 | B5 exhaust temperature sensor fault alarm | - | - | - | - | 1 | 1x0019 | 0 | WIFI upload
AL76 | B8 return air temperature sensor fault alarm | - | - | - | - | 1 | 1x0020 | 0 | WIFI upload
AL79 | Abnormal water pump duty cycle | - | - | - | - | 1 | 1x0021 | 0 | WIFI upload
AL98 | Compressor variable frequency drive board fault alarm | - | - | - | - | 1 | 1x0022 | 0
AL57 | Communication failure between the main control board and the driver board | - | - | - | - | 1 | 1x0023 | 0 | WIFI upload
WN01 | Indoor pipeline antifreeze protection alarm | - | - | - | - | 1 | 1x0024 | 0 | WIFI upload
ALEP | Main control board memory EPROM failure | - | - | - | - | 1 | 1x0025 | 0
AL100 | IPM overcurrent | - | - | - | - | 1 | 1x0026 | 0
AL101 | Compressor drive failure | - | - | - | - | 1 | 1x0027 | 0
AL102 | Compressor overcurrent | - | - | - | - | 1 | 1x0028 | 0
AL103 | Input voltage phase loss | - | - | - | - | 1 | 1x0029 | 0
AL104 | IPM current sampling fault | - | - | - | - | 1 | 1x0030 | 0
AL105 | Radiator overheating shutdown | - | - | - | - | 1 | 1x0031 | 0
AL106 | Precharge failed | - | - | - | - | 1 | 1x0032 | 0
AL107 | DC bus overvoltage | - | - | - | - | 1 | 1x0033 | 0
AL108 | DC bus undervoltage | - | - | - | - | 1 | 1x0034 | 0
AL109 | AC input undervoltage | - | - | - | - | 1 | 1x0035 | 0
AL110 | AC input overcurrent | - | - | - | - | 1 | 1x0036 | 0
AL111 | Input voltage sampling failure | - | - | - | - | 1 | 1x0037 | 0
AL112 | DC fan 1 fault | - | - | - | - | 1 | 1x0038 | 0
AL113 | Temperature sensor failure | - | - | - | - | 1 | 1x0039 | 0
AL114 | DC fan 2 fault | - | - | - | - | 1 | 1x0040 | 0
AL115 | Communication with the main control board is abnormal | - | - | - | - | 1 | 1x0041 | 0
AL00 | Communication failure between the main control board and the screen | - | - | - | - | 1 | 1x0042 | 0
AL202 | IO Board: Solar Temperature Sensor Failure | - | - | - | - | 1 | 1x0043 | 0
AL203 | IO board: Low temperature partition B4 temperature sensor failure | - | - | - | - | 1 | 1x0044 | 0
AL204 | IO board: High temperature partition B5 temperature sensor failure | - | - | - | - | 1 | 1x0045 | 0
AL133 | IPM module overheating shutdown | - | - | - | - | 1 | 1x0046 | 0
AL134 | Compressor model failure | - | - | - | - | 1 | 1x0047 | 0
AL77 | External coil temperature sensor fault alarm | - | - | - | - | 1 | 1x0053 | 0
AL22 | High voltage switch fault alarm | - | - | - | - | 1 | 1x0054 | 0
AL39 | The 24h high voltage switch fault alarm exceeds the specified number of times | - | - | - | - | 1 | 1x0055 | 0
Control switch
| Air conditioner on/off | 0 (off) | 0 (off) | 1 (Power on) | - | 1 | 0X0001 | 0 | WIFI upload
| Hot water switch | 0 (off) | 0 (off) | 1 (Power on) | - | 1 | 0X0002 | 0
SF201 | Power lock function switch | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0003 | 0
SF217 | SG function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0005 | 0
SF41 | EEV1 manual setting switch | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0006 | 2
SF42 | EEV2 manual setting switch | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0007 | 2
SF58 | EEV forward and reverse | 0 (forward) | 0 (forward) | 1 (reverse) | - | 1 | 0X0008 | 2
SF216 | Compressor frequency manual setting switch | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0009 | 2
SF221 | Current limiting function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0010 | 2
SF10 | Water pump configuration | 0 (external) | 0 (external) | 1 (built-in) | - | 1 | 0X0013 | 1
EV01 | Pump operation mode | 0 (continuous operation) | 0 (continuous operation) | 1 (auto start/stop) | - | 1 | 0X0014 | 1
SF46 | Water flow fault shielding switch | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0015 | 2
SF50 | EVI function enabled | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0016 | 2
SF59 | EVI forward and reverse | 0 (forward) | 0 (forward) | 1 (reverse) | - | 1 | 0X0017 | 2
SF60 | Pressure sensor selection | 0 (integrated) | 0 (integrated) | 1 (split) | - | 1 | 0X0018 | 2
SF57 | Troubleshooting | 0 (do not clear) | 0 (do not clear) | 1 (clear) | - | 1 | 0X0019 | 2
SF48 | Manual defrost function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0020 | 2
SF222 | Cancel the forced defrost function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0021 | 2
SF219 | Displays cumulative heat generation and power consumption | 0 (not displayed) | 0 (not displayed) | 1 (display) | - | 1 | 0X0023 | 2
SF53 | New ID address selection (domestic sales) | 0 (off) | 0 (off) | 1 (On) | - | 1 | 0X0024 | 2
SF113 | DI input mode selection function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0025 | 2 | 1 is cooling (short circuit) 0 is heating (not connected)
SF112 | Manual electric heating function/air conditioning electric heating configuration selection | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0026 | 1 | Display
SF223 | Debug Mode | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0027 | 2
SF110 | Night mode status | 0 (off) | 0 (off) |  | - | 1 | 0X0028 | 0
| 24-hour alarm manual reset mode selection | 1 (on) | 0 (off) | 1 (on) | - | 1 | 0X0029 | 2
SF216_2 | Compressor frequency manual setting switch 2 | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0030 | 2 | System 2
SF224 | Boiler switching function | 0 (off) | 0 (off) | 1 (on) | - | 1 | 0X0031 | 2
SF56 | Accumulated heat generation and accumulated power consumption are reset to zero | 0 (do not clear) | 0 (do not clear) | 1 (clear) | - | 1 | 0X0032 | 2
SF61 | Photovoltaic signal | 0 (disconnected) | 0 (disconnected) | 1 (On) | - | 1 | 0X0033
SF114 | Hot water electric heating configuration selection | 0 (none) | 0 (none) | 1 (yes) | - | 1 | 0X0034 | 1
Appendix 1:
Appendix 2:
| Water pump model | Heat pump model | Heat pump classification
| UPM3K | CHS06V | Chiller
CHS08V
CHS10V
CHS12V
| UPML/UPMXL | CHS15V
| UPMF20-125-PCI | CHS22V
| HBGF 25-80-130 | HS06V | Heat pumps (orders before 2025)
HS08V
HS10V
HS12V
| HBF 25-105-130 | HS15V
| HBGF25-125-130 | HS22V
| APF 25-8-130E | HS06V | Heat pumps (orders after 2025)
HS08V
HS10V
HS12V
| APF 25-10-130E | HS15V
| APF 25-12-130E | HS22V
| other | - | -
When the user chooses to connect an external water pump, he can select the "other" water pump type, and the unit will detect the system water flow signal in the form of a water flow switch;